SHORT TENDER NOTICE NO.08/2009
(PURCHASE OF 100 KVA DIESEL GENERATORS)
Sealed bids are invited from the firms having registration with the Sales Tax and Income Tax Departments for supply & installation (at Islamabad) of three (03) 100 KVA Diesel Generators Sets. Detail specifications and terms & conditions may be obtained either from the office of undersigned (during working hours) or download from www.ppra.org.pk or www.pral.com.pk from 08/08/2009 to 26/08/2009. Last date for submission of the bids is 26/08-2009 on or before 1200 hours. Bids shall be opened on the same day at 1230 hours. 

Manager (Administration)

House # 15, Street # 19, F-6/2, Islamabad.

Ph:051-9208687

TENDER DOCUMENT

PAKISTAN REVENUE AUTOMATION (PVT.) LIMITED

Ref. Proc-Generator/PRAL/2009       

    

       
         
   August 08, 2009
Subject:
TENDER NO. 08/2009 DATED 8TH AUGUST 2009 ___________FOR THE SUPPLY & INSTALLATION / COMMISSIONING / TESTING OF THREE (03) 100 KVA DIESEL GENERATORS AT PRAL OFFICES IN ISLAMABAD
1.
Pakistan Revenue Automation (Pvt.) Ltd. (hereinafter called PRAL/Purchaser) invites sealed bids for supply / installation / commissioning / testing of three (03) 100 KVA Diesel Generators Sets for PRAL offices located in Islamabad. Detail specifications of the Generators are given in the Schedule of Requirement attached at Annexure “A”.

2.
If you have any doubt as to the meaning of any portion of the technical specifications, you may seek clarification of the same from Mr. Ali Hameed, Director Network and Infrastructure on Phone # 051-9204952 / 051-9206777 and Cell # 0321-5591498.
3.
PRAL reserves the right to increase or decrease the quantity of equipment or may cancel any or all items shown in Annexure “A” and to accept Bid (s) separately for each item in the Annexure “A”, accept or reject any bid to be received against this tender inquiry, annul the bidding process and reject all bids at any time prior to award of Contract (s) without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected Bidder or of the grounds for PRAL’s action. 
4.
Income Tax / Withholding Tax will be deducted in accordance with the law. Kindly note that the Sales Tax shall also be deducted in accordance with the law.  
5.
DELIVERY SCHEDULE 


The delivery / installation / commissioning / testing of the equipment mentioned in the attached Annexure “A” is required ON MOST URGENT BASIS. So the lowest technical compliant bidder(s) may be in a position to deliver/install/commission/test the equipment immediately after award of the contract(s), therefore the bidders are required to quote shortest possible delivery & installation/commissioning / testing time.
6.
PENALTY:

For failure to comply with the delivery schedule of Purchase Order (s), to be issued against this tender documents penalty will be imposed on defaulting Supplier as under:

6.1
1% of the cost of entire purchase order or of such item as remains un-supplied/un-completed for every day up to maximum of 5% for 10 days exceeding the delivery period.

6.2
If the item is not supplied even after payment of penalty for 10 consecutive days PRAL reserves the right to cancel the purchase order and to purchase required equipment from elsewhere at risk and cost of the defaulting Supplier.

7.
Quoted prices must be inclusive of all taxes (Income Tax and Sales Tax), indicating unit price and total bid price.

8.
Price must be quoted including all charges like handling, loading, transportation, unloading of the equipment at Islamabad. Quoted prices must also be inclusive of cost for the free maintenance of equipment on installation site during warranty period. 

9.
Bidding Form must also be duly filled in, stamped and signed by authorized representative of the bidder.

10.
Quoted price shall be valid for six (6) months from the opening date of the bids. However, any subsequent change in taxes and duties as notified by Federal Board of Revenue will be given due consideration.

11.
EARNEST MONEY:

The Bidder shall furnish as part of his bid, a Call Deposit/Pay Order equivalent to 2% of the total bid value as Earnest Money crossed in favour of “Pakistan Revenue Automation (Pvt.) Ltd.”. Bank Guarantee as earnest money will not be entertained. Any bid not accompanied by Earnest Money shall be rejected without any right of appeal. In case of cancellation of Purchase Order as default of the Supplier the earnest money shall be forfeited in favour of PRAL. 
12.
If the Purchase Order is cancelled due to any fault / default of the successful bidder, the Earnest Money shall be forfeited 
13.
PAYMENT:

100% payment of the total value of the bill/purchase order will be released subject to:

13.1.
Completion of the delivery/installation/commissioning/testing of the equipment in accordance with the specifications mentioned in this tender document or Purchase Order(s) to be issued against this tender;

13.2.
Submission of Bank Guarantee (to be issued by any renowned schedule bank), being 10% of the total bill value for the warranty period. The Bank Guarantee shall be released after successful completion of warranty period. Failing to provide bank guarantee 10% of the bill shall be retained till to the successful expiry of the warranty period;

14.
SEALING AND MARKING OF BIDS.

14.1
The bids shall be submitted in sealed envelope marked as under:

Manager (Administration)

House # 15, Street # 19, F-6/2, Islamabad.

14.2
The envelopes shall also bear the word “CONFIDENTIAL” and following identifications:-

BID NO. 08/2009
For supply & installation of 100 KVA Diesel Generators.
15.
DEADLINE FOR SUBMISSION OF BIDS:


All bids must be delivered in the Office of undersigned on or before the prescribed deadline of 1200 hours on 26-08-2009.
15.
OPENING OF BIDS:


The Purchaser will open the bids in the presence of bidder representatives who choose to attend at 1230 hours on 26-08-2009 at the below mentioned address. 

16.
WARRANTY

16.1
The Supplier shall warrant that all equipment supplied against the Purchase Order (s) shall have no defect arising from design, materials or workmanship or from any act or omission of the Supplier that may develop under normal use of the supplied items under the conditions prevailing at final destination.

16.2
Period of Warranty and maintenance with labour and material cost shall be minimum “one (01) year comprehensive” for Diesel Generators and remaining equipment. 

During warranty period the supplier will be responsible to repair/replace the faulty equipment on installation place free of cost within 24 hours after occurrence of fault. During warranty period due to any reason, if the Supplier failed to rectify the problem, PRAL shall repair the equipment or replace the defective parts thereof and forfeit the Bank Guarantee/retained values.   

17.
All bids should include:
17.1
Company’s profile, list of clients with their telephone number and address;  

17.2
Copies of Income Tax and Sales Tax registration certificates;

17.3
Copy of dealership certificate (issued by the Manufacturer); 
17.4
A call deposit being, 2% of the total bid value, as Earnest Money crossed in favour of “Pakistan Revenue Automation (Pvt.) Ltd.; and 

17.5
Brochures and other technical material of the quoted equipment.

18.
PRAL reserves the right to increase or decrease the quantity of the equipment / or scope of work or may cancel any or all tender work shown in Annexure “A”.   
(SOHAIL AKHTAR)

Manager (Administration)

House # 15, Street # 19, F-6/2, Islamabad.

Phone:
9208687
ANNEXURE-A

BILL OF QUANTITY (BOQ):
TENDER # 08/2009, DATED 08-08-2009
	S. No
	DESCRIPTION
	QTY

	1
	100 KVA SNMP enabled FG Wilson or any internationally recognized brand Diesel Generator with Super Silenced Canopy and other works as per specifications given below. (Turnkey Installation Testing and Commissioning).
	03


100 KVA Diesel Generator FG Wilson or any Internationally recognized brand 

· 3 Phase (115 Ampere per Phase Out put)
· Rated Frequency (Hz) 50-60 Hz

· Rate Voltage (AC) (V) 400 / 230

· Auto Voltage Regulator (AVR)

· Automatic Voltage Selector Switch

· Rated Current (AC) (A) 288

· Power Factor (COSΦ)  0.8 (lag) 

· Power Supply AC, 3-phase, 4-lines 

· Type In-line, 4-strokes, water cooled, direct injection, diesel engine 

· Number Of Cylinders: 4 / In line.
· Horsepower: 200 approx 

· Voltage Regulator

· Phase Selector

· Voltmeter

· Fuel Tank Capacity: 227 Liters

· Fuel Indicator

· Safety shutdown for Oil Pressure, Water Temperature, Warning Lights indicate abnormal conditions

· Simple, easy to read instrumentation panel provides quick, accurate information about both generator and engine performance

· Ammeter

· Frequency Meter

· Pilot Light

· Circuit Breaker

· Rated Rotation Speed (r/min) 1500

· Starting Method Electric starting 

· Cooling Method Closed cycle water-cooled

· Air Intake Type Natural

· Speed Regulation Mechanical/Electrical

· Alternator Model: As per Original Equipment Manufacturer
· Excitation Mode Brushless

· Insulation Class F

· Oil Pressure indicator

· Water Temp.

· Hour Meter

· Start Switch

· Preheat Indicator

· Emergency Shutdown

· Monitors & Controls

· Water / Fuel Separator

Auto Transfer Switch Panel

· Standard time delay neutral for reduced switchover problems

· Logic control with inphase monitor and adjustable settings with LED indicators

· Control switch located on front of the door for easy operation

· 160-millisecond transfer time

· Manual 3-position selector switch

· Circuit breaker protected

· Single coil design, electrically operated and mechanically held

· Programmable exerciser

· Main contacts are silver alloys to resist welding and sticking

· Conformal coatings protects all printed circuit boards

· Indicating LED’s for switch position-Normal, Emergency & Standby operating

· Enclosure with hinged door and key- locking handle

· Three position switch

Super-Silenced Acoustic Canopy

· Base frame of canopy made from 4mm thick MS sheet.
· Super structure doors & roof top made from 2.5 mm thick MS sheet.
· Canopy completely insulated with 1 layer of 75 mm x 100” kg / cum density Rock wool and 1 layer of 15 mm thick felt to reduce maximum sound.
· Insulation retained with 22 SWG MS perforated sheet of 4mm holes 60% perforation.
· Fresh air provided through Acoustic Louvers.
· No duration during running of DG Set with all the doors closed with in ambient temperature of 40 degree C.
· Radiator exhaust outlet through Acoustic Louvers and up ward Acoustic duct to control out going noise.
· Hinged and lockable door all around Canopy for easy access to DG Set for routine maintenance.
· Doors will be sealed with heat resistant imported self gripping rubber gas kit.
· Stainless steel hinges with greasing nipple.

· Canopy structure Skid mounted type.

· 4 Nos of heavy duty lifting eyes for Canopy lifting.

· Internal engine exhaust line insulated with heat resistant fiber glass tape of 4mm thick x 75mm wide.

· Sound level within 72 dB (A) at 1 meter.

· IP 33 standard.

· Two stage critical type Silencer mounted inside the Canopy.

· DG Set can be easily removed for any major over hauling.

· Canopy painted with two coats of Epoxy primer and final painted with two coats of chemical resistant Epoxy paint.

Cable

· 70mm 4 core PVC/PVC with GI Conduit  250m x 2 Non-Armored and should be ISO certified with applicable BS standards.

Installation

RCC foundation and unit earthing with (LxWxT) 1000mm x 1000mm x 12mm with 50mm PVC coated branded grounding wire (2 earthpits minimum) and commissioning.

BIDDING FORM
Dated 08-08-2009    




                                  Tender No.08/2009
Pakistan Revenue Automation (Pvt.) Limited, Islamabad.

Gentlemen,

1.
Having examined the conditions to Tender and Specifications of Tender No.08/2009 dated 08-08-2009 the receipt of which is hereby acknowledged we, the undersigned, offer to , supply / install / commissioning / testing in conformity with specifications mentioned in Annexure “A” and conditions of Tender for the sum of Rs._________________________ (Rupees ______________________________ ) or such other sums as may be ascertained in accordance with the said Conditions.

2.
If our Bid is accepted we shall deliver / commenced the equipment / services mentioned in the tender documents within ______ days from the date of receipt of your firm Purchase Order / Work Order.

3.
We agree to abide by the terms and conditions of the Tender for the period of _______ from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.

4.
Until a formal Purchase order(s) is placed, this Bid, together with your written acceptance thereof, shall constitute a binding contract between us.

5.
We understand that you are not bound to accept the lowest or any proposal you may receive or to inform us of the rejection of our bid or to give any reasons therefore.

Dated this ______________________ day of ______________________________ 2009_______________.

Signature _______________________ in the capacity of ______________________________ duly authorized to sign Tender for and on behalf of 

_____________________________________________________________________________________

(NAME OF FIRM IN BLOCK CAPITALS)

Complete address:________________________________________________________________________

Fax No.____________________________ Telephone No.______________________________________

______________________

( SIGNATURE )Witness:-

1.
_______________________

2.
_______________________
