SHORT TENDER NOTICE NO.ADMIN(G-09)/2012

Sealed bids are invited from the firms registered with the sales tax and income tax department for IMMEDIATE supply and installation of 80KVA UPS. Tender Documents containing terms & conditions and technical details may be obtained from the office of undersigned (during office hours) or may download from www.ppra.org.pk or www.pral.com.pk from 26/11/2012 to 10/12/2012. Last date for submission of bids is 10/12/2012 on or before 1200 hours. The bids shall be opened on 10/12/2012 at 1230 hours in the presence of the bidder’s representatives.

Manager (Procurement)

House # 2-A, Embassy Road, Sector G-6/4, Islamabad.

Ph: 051-9208687

TENDER DOCUMENT

PAKISTAN REVENUE AUTOMATION (PVT.) LIMITED

Ref. Proc-/UPS/PRAL/2012       		    		       	         	 	 		 November 26, 2012

Subject:	TENDER NO. ADMIN(G-09)/2012 DATED 26/11/2012 FOR THE SUPPLY & INSTALLATION OF 80 KVA UPS

1.	Pakistan Revenue Automation (Pvt.) Ltd. (hereinafter called PRAL/Purchaser) invites sealed bids for immediate supply & installation (at Islamabad) of one (01) 80 KVA UPS. Detail specifications of the UPS are given in the Schedule of Requirement attached at Annexure “A”.

2.	If you have any doubt as to the meaning of any portion of the technical specifications, you may seek clarification of the same from Malik Nasir Abbas, Manager (Infrastructure) PRAL Cell # 0321-5371151.

3.	PRAL reserves the right to increase or decrease the quantity, annul the bidding process and accept or reject any or all bids for which reasons on request shall be communicated to the concerned bidder.

4.	Income Tax / Withholding Tax will be deducted in accordance with the law. Kindly note that the Sales Tax shall also be deducted in accordance with the law.

5.	DELIVERY SCHEDULE

The delivery / installation (at Islamabad) of the UPS mentioned in the attached Annexure “A” is required on MOST URGENT BASIS. The UPS must be available as “Ex-Stock therefore only the bidder(s) who offered EX-Stock delivery will be entertained / considered.

6.	PENALTY:

For failure to comply with the delivery schedule of Purchase Order (s), to be issued against this tender documents penalty will be imposed on defaulting Supplier as under:

6.1	1% of the cost of entire purchase order or of such item as remains un-supplied/un-completed for every day up to maximum of 5% for 10 days exceeding the delivery period.

6.2	If the item is not supplied even after payment of penalty for 10 consecutive days PRAL reserves the right to cancel the purchase order and to purchase required equipment from elsewhere at risk and cost of the defaulting Supplier.

7.	Quoted prices must be inclusive of all taxes (Income Tax and Sales Tax), indicating unit price and total bid price.

8.	Price must be quoted including all charges like handling, loading, transportation, unloading of the equipment at Islamabad. Quoted prices must also be inclusive of cost for the free maintenance of equipment on installation site during warranty period.

9.	Bidding Form must also be duly filled in, stamped and signed by authorized representative of the bidder.

10.	Quoted price shall be valid for 90 days from the opening date of the bids. However, any subsequent change in taxes and duties as notified by Federal Board of Revenue will be given due consideration.

11.	EARNEST MONEY:

The Bidder shall furnish as part of his bid, a Call Deposit/Pay Order equivalent to 2% of the total bid value as Earnest Money crossed in favour of “Pakistan Revenue Automation (Pvt.) Ltd.”. Bank Guarantee as earnest money will not be entertained. Any bid not accompanied by Earnest Money shall be rejected without any right of appeal. In case of cancellation of Purchase Order as default of the Supplier the earnest money shall be forfeited in favour of PRAL.

12.	PAYMENT:

100% payment of the total value of the bill/purchase order will be released subject to:

12.1.	Completion of the delivery/installation of the equipment in accordance with the specifications mentioned in this tender document or Purchase Order(s) to be issued against this tender;

12.2.	Submission of Bank Guarantee (to be issued by any renowned schedule bank), being 10% of the total bill value for the warranty period. The Bank Guarantee shall be released after successful completion of warranty period. Failing to provide bank guarantee 10% of the bill shall be retained till to the successful expiry of the warranty period;

13.	SEALING AND MARKING OF BIDS.

13.1	The bids shall be submitted in sealed envelope marked as under:

Manager (Procurement)

House # 2-A, Main Embassy Road, Sector G-6/4, Islamabad.

13.2	The envelopes shall also bear the word “CONFIDENTIAL” and following identifications:-

BID NO. ADMIN (G-09)/2012

For supply & installation of 80 KVA UPS.

14.	DEADLINE FOR SUBMISSION OF BIDS:

All bids must be delivered in the Office of undersigned on or before the prescribed deadline of 1200 hours on 10/12/2012.

15.	OPENING OF BIDS:

The Purchaser will open the bids in the presence of bidder representatives who choose to attend at 1230 hours on 10/12/2012 at the below mentioned address.

16.	WARRANTY

16.1	The Supplier shall warrant that all equipment supplied against the Purchase Order (s) shall have no defect arising from design, materials or workmanship or from any act or omission of the Supplier that may develop under normal use of the supplied items under the conditions prevailing at final destination.

16.2	All components of the UPS system (UPS module, batteries and optional cabinet) shall be covered by a standard one (01) year comprehensive warranty with On-site support, 24x7 on-site service/support with guaranteed response times not greater than 2 hours.

During warranty period the supplier will be responsible to repair/replace the faulty equipment on installation place free of cost within 24 hours after occurrence of fault. During warranty period due to any reason, if the Supplier failed to rectify the problem, PRAL shall repair the equipment or replace the defective parts thereof and forfeit the Bank Guarantee/retained values.

17.	All bids should include:

17.1	Company’s profile, list of clients with their telephone number and address;

17.2	Copies of Income Tax and Sales Tax registration certificates;

17.3	A call deposit being, 2% of the total bid value, as Earnest Money crossed in favour of “Pakistan Revenue Automation (Pvt.) Ltd.; and

17.4	Brochures and other technical material of the quoted equipment.

18.	PRAL reserves the right to increase or decrease the quantity of the equipment / or scope of work or may cancel any or all tender work shown in Annexure “A”.

# (SOHAIL AKHTAR)

Manager (Procurement)

House # 2-A, Main Embassy Road, Sector G-6/4, Islamabad.

Phone: 9208687

ANNEXURE-A

TENDER # ADMIN (G-09)/2012, DATED 26/11/2012

Bill of Quantity

ANNEXURE-A

TECHNICAL SPECIFICATIONS

80-KVA TRUE ON-LINE DOUBLE CONVERSION PURE SINE WAVE TELCO CLASS HIGH EFFICIENCY DATA CENTER UPS

SUMMARY

A Three-phase continuous duty, on-line, doubles conversion, solid-state uninterruptible power system, hereafter referred to as the UPS. The UPS shall consist of the UPS module with maintenance bypass, battery backup, and other features as described in this specification.

UPS SYSTEM DESCRIPTION

- UPS System Components:

The UPS system shall consist of the following main components:

- UPS module containing a Rectifier, Inverter, Battery Charger, Static Bypass, Integrated maintenance bypass, and associated Control and Monitor Panel.

- Battery string(s) in Line-and-Match Battery Cabinets or racks.

- Optional Line-and-Match cabinet(s).

- UPS Module Modes of Operation:

The UPS Module shall operate as frequency independent (class VFI-SS-111), fully automatic online system in the following modes:

- Normal: Utilizing commercial AC power, the critical load shall be continuously supplied by the Inverter. The Inverter shall power the load while regulating both voltage and frequency. The Rectifier shall derive power from the commercial AC source and shall supply DC power to the Inverter. Simultaneously, the Battery Charger shall charge the battery.

- Battery: Upon failure of the commercial AC power, the critical load shall continue to be supplied by the Inverter, which shall obtain power from the batteries without any operator intervention. There shall be no interruption to the critical load upon failure or restoration of the commercial AC source.

- Recharge: Upon restoration of the AC source, the Charger shall recharge the batteries and simultaneously the Rectifier shall provide power to the Inverter. This shall be an automatic function and shall cause no interruption to the critical load.

- Bypass: If the UPS module must be taken out of the Normal mode for overload, load fault, or internal failures, the static bypass switch shall automatically transfer the critical load to the commercial AC power. Return from Bypass mode to Normal mode of operation shall be automatic. No break transfer to and from Bypass mode shall be capable of being initiated manually from the front panel.

AGENCY CERTIFICATIONS

- Safety UL1778, Cul, EN62040-1-1 and EN500091-2.

- EMC IEC62040-2 EN50091 Class A (restricted access)

- Surge ANSI C62, 41 Cat, A&B

ENVIRONMENTAL REQUIREMENTS

- The UPS shall withstand any combination of the following external environmental conditions without operational degradation.

- Operating Temperature: 0 degrees C to + 40 degrees C without de-rating (excluding batteries).

- Relative Humidity: (operating and storage): 95% maximum non-condensing.

- Elevation: Operational: 6600 ft (2000 m) maximum without de-rating.

UPS EFFICIENCY

- Normal Mode 94%.

- Efficiency Mode 99%

UPS RATING AND GENERAL OPERATING CHARACTERISTICS

- Power Factor 0.9

- Apparent Power 80-KVA

- Active Power  72-KW

- Intelligent power interface with management software

- Capable of remote monitoring & Management

- EPO capable (Emergency Power Off)

- Built-In protection against surges, spikes, over & under voltage and short circuit protection.

- Built-in stabilizer.

- Cold start facility.

- Capable of parallel attachment (N+1) of up-to 4 units in load. (Parallel add in facility of new UPS in the existing environment).

- Hot stand-by redundant & parallel function.

INPUT CHARACTERISTICS

- Nominal three phase input voltage: 400 VAC – 4-wire plus ground for 4-wire plus ground output configuration

- Operating input voltage range: + 10%, - 15% of average nominal input voltage without battery discharge.

- Operating input frequency range shall be 45 to 55Hz.

- Input power factor 0.99 lagging.

- Input current distortion <4.5% (no input filter required)

- Soft start capability

- Internal backfeed protection

- Broadcast global support

OUTPUT CHARACTERISTICS

- Nominal output voltage 400V, 3-phase, 4 wire plus ground.

- Regulation ±1%

- Inverter PWM with IGBT switching

- Voltage THD <2% (100% linear load); <5% (non-linear load)

- Load power factor range: Down to 0.9 pf

- Manual output voltage adjustment shall be +/- 3% from nominal.

- Line synchronization range shall be +/- 3Hz, adjustable to +/- 5Hz.

BATTERY

- Battery types VRLA or AGM & Gel

- Battery voltage 384-480V

- Battery overcharging protection.

- Charging method: Advanced battery management

- Heat dissipation <48 BTU @ full load

- Scheduling facility for battery testing & UPS controls.

WARRANTY

All components of the UPS system (UPS module, batteries, and optional cabinet) shall be covered by a standard 1-year warranty with On-site support, 24x7 on-site service / support with guaranteed response times not greater than 2 hours.

TURNKEY INSTALLATION OF THE UPS

Complete turkey installation/ commissioning of the UPS complete in all respect which includes 30 FT” 50mm2 four core PVC/PVC 99.99% (Pakistan cable) for input and output circuits and necessary jobs for commissioning.

BILL OF QUANTITY

| S. No | DESCRIPTION | Quantity |
| --- | --- | --- |
|  | 80 KVA Telco Class Industrial Grade UPS with turnkey installation & onsite support with 1 year comprehensive warranty | 1 |

BIDDING FORM

##### Dated 26/11/2012

##### Tender No.ADMIN (G-09)/2012

Pakistan Revenue Automation (Pvt.) Limited, Islamabad.

Gentlemen,

1.	Having examined the conditions to Tender and Specifications of Tender No.ADMIN (G-09)/2012 dated November 26, 2012 the receipt of which is hereby acknowledged we, the undersigned, offer to install, supply and deliver in conformity with specifications mentioned in Annexure “A” and conditions of Tender for the sum of Rs._________________________ (Rupees ______________________________ ) or such other sums as may be ascertained in accordance with the said Conditions.

2.	If our Bid is accepted we shall deliver / commenced the equipment / services mentioned in the tender documents within ______ days from the date of receipt of your firm Purchase Order / Work Order.

3.	We agree to abide by the terms and conditions of the Tender for the period of _______ from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.

4.	Until a formal Purchase order(s) is placed, this Bid, together with your written acceptance thereof, shall constitute a binding contract between us.

5.	We understand that you are not bound to accept the lowest or any proposal you may receive or to inform us of the rejection of our bid or to give any reasons therefore.

Dated this ______________________ day of ______________________________ 2012_______________.

Signature _______________________ in the capacity of ______________________________ duly authorized to sign Tender for and on behalf of

_____________________________________________________________________________________

(NAME OF FIRM IN BLOCK CAPITALS)

Complete address:________________________________________________________________________

Fax No.____________________________ Telephone No.______________________________________

______________________

( SIGNATURE )

Witness:-

1.	_______________________

2.	_______________________