TENDER DOCUMENT

PAKISTAN REVENUE AUTOMATION (PVT.) LIMITED

Tender No. P-30/2018

Dated 13-12-2018

BIDS SUBMISSION: 28-12-2018 ON OR BEFORE 1100 HOURS

BIDS OPENING DATE AND TIME: 28-12-2018 AT 1130 HOURS

Subject: 	TENDER NO. P-30/2018 DATED 13-12-2018 FOR THE SUPPLY AND INSTALLATION OF POWER MODULE FOR APC UPS:

1.	Pakistan Revenue Automation (Pvt.) Ltd. (hereinafter called PRAL) invites sealed Proposals from the registered with the Sales Tax and Income Tax departments for Supply, and Installation of Power Module for APC UPS at Customs House, Karachi as per specifications and criteria described in “Annexure-A”.

2. 	If you have doubt as to the meaning of any portion of the specifications or other terms and conditions you may seek clarification of the same from Mr. Ali Hameed, Chief Manager (Networks & Infrastructure) PRAL, Islamabad, on Cell # 0300-0240565.

3. 	The successful vendor will be responsible to deliver and install the Power Module for APC UPS. Quoted prices must be inclusive of installation charge.

4.	PRAL reserves the right to increase or decrease the quantity mentioned in the Schedule of Requirement Annexure “A”, accept or reject any bid to be received against this tender inquiry, annul the bidding process and reject all bids at any time prior to award of Contract (s).

5. 	DELIVERY SCHEDULE:

The delivery/installation of Power Module for APC UPS is required within 4-6 weeks.

6. 	PENALTY:

For failure to comply with the delivery schedule of Purchase Order (s), penalty will be imposed on defaulting Supplier as under:

6.1 	1% of the cost of entire purchase order or of such equipment as remains un-supplied/un-completed for every day up to maximum of 5% for 10 days exceeding the delivery period.

6.2 	If the solution is not supplied even after payment of penalty for 10 consecutive days PRAL reserves the right to cancel the purchase order and to purchase required equipment from elsewhere at risk and cost of the defaulting Supplier.

7. 	Income Tax / Withholding Tax will be deducted in accordance with the law. Kindly note that the Sales Tax shall also be deducted in accordance with the law.

8. 	Price must be quoted including all charges like Supply and Installation of Power Module for APC UPS at the location as mentioned above.

9. 	Quoted price shall be valid for 180 days from the opening date of the bids. However, any subsequent change in taxes and duties as notified by Federal Board of Revenue will be given due consideration.

10. 	Bidding Form as per Annexure “B” must also be duly filled in, stamped and signed by authorized representative of the bidder.

11. 	EARNEST MONEY:

11.1 	The Bidder shall furnish as part of his bid, a Call Deposit/Pay Order equivalent to 2% of the total bid value as Earnest Money crossed in favor of “Pakistan Revenue Automation (Pvt.) Ltd.”. Any bid not accompanied by Earnest Money shall be rejected without any right of appeal.

11.2 	Part earnest money or crossed Cheque/bank guarantee, as earnest money is not acceptable.

11.3 	In case of cancellation of Purchase Order as default of the Supplier the earnest money shall be forfeited in favor of PRAL.

12. 	PAYMENT:

90% payment of the total value of the bill/purchase order will be released after supply and installation of Power Module for APC UPS in accordance with the Purchase Order and remaining 10% shall be released after completion of warranty period or submission of Bank Guarantee, being 10% of the total bill value. The bank guarantee must be issued by renowned schedule bank. The bank guarantee shall be released after successful completion of warranty period.

13. 	Warranty and Support of the Power Module for APC UPS must be three (3) years comprehensive, onsite with parts & labor. The bidder must be authorized partner of OEM. During the support period if the partner is unable to resolve the issue then OEM must be engaged for resolution of issue.

14. 	SEALING AND MARKING OF BIDS.

14.1 The bids shall be submitted in sealed envelope marked as under:

MANAGER (P&I)

PAKISTAN REVENUE AUTOMATION (Pvt.) LIMITED

2nd Floor, Software Technology Park (STP), Sector, I-9/3, Islamabad.

14.2 The envelopes shall also bear the word “CONFIDENTIAL” and following identifications: -

Bid No. P-30/2018 dated 13-12-2018

For the supply and installation of Power Module for APC UPS

14.3 If the envelope is not marked, as instructed above, the PRAL will assume no responsibility for the misplacement or premature opening of the bid.

15. 	DEADLINE FOR SUBMISSION OF BIDS:

All bids/Proposals must be delivered in the office of undersigned on or before the prescribed deadline of 1100 hours on 28-12-2018.

16.	 LATE PROPOSALS:

Any bid received by the PRAL after the prescribed deadline will be returned unopened to the Bidder.

17. 	OPENING OF BIDS:

The Purchaser will open the bids in the presence of bidder’s representatives who choose to attend at 1130 hours on 28-12-2018 in the office of undersigned at 2nd Floor, Software Technology Park (STP), Sector, I-9/3, Islamabad.

18. 	EVALUATION:

18.1. 	After opening, PRAL will examine the bids for technical evaluation and completeness of the same as per tender requirements.

18.2. 	Bidder (s) who does not qualify cannot challenge the findings of the evaluation or ask for reasons of disqualification.

19.	 INSPECTION AND TESTS:

19.1. 	PRAL’s representative shall have the right to inspect and / or test the equipment/solution to confirm their conformity to Purchase Order (s) specifications.

19.2. 	Should any inspected or tested item fail to conform to the specifications, PRAL may reject it and the Supplier shall either replace the rejected equipment or make all alterations necessary to meet specification of PRAL. All costs incurred on such replacements / alterations shall be entirely borne by the Supplier. Failing to do so the Purchase Order (s) will be cancelled and all retained values of the defaulter will be forfeited in favor of PRAL.

20. WARRANTY:

20.1 	The Supplier shall warrant that all material supplied under the Contract (s) shall have no defect arising from design, materials or workmanship or from any act or omission of the Supplier, that may develop under normal use of the supplied items under the conditions prevailing at final destination.

20.2 	PRAL shall promptly notify the Supplier in writing of any claims arising under this Warranty. Upon receipt of such notice, the Supplier shall repair or replace the defective equipment or parts thereof, without cost to PRAL immediately.

20.3 	Period of comprehensive warranties and support with labor and material cost shall be three (3) years comprehensive (with labor & parts). The supplier shall be responsible for providing “warranty and comprehensive” of the Power Module for APC UPS to be installed.

During the warranty period due to any reason, if the Supplier failed to rectify the problem, PRAL shall get repair the equipment or replace the defective parts thereof and forfeit the Bank Guarantee/retained values. During the warranty and support period bidder will be responsible to provide any major/minor upgrade as released by OEM without any additional cost.

21. 	All bids should include:

- Company’s profile, list of such projects handled, list of clients with telephone numbers and addresses.

- Copies of Income Tax and Sales Tax registration certificates.

- Affidavit (on legal paper) to the effect that the firm has never been black- listed by any agency of government/semi government/autonomous or business concern.

- Earnest Money 2% of total bid value.

- Draft SLA.

- Annual Turnover and Audit Report of previous financial year.

- Details of Technical Resources with certifications.

- Project Specific Certified Resources.

- Working office in Islamabad with address Proof.

- List of major projects.

- Complete Client Details.

- Reference letter from the clients

22. 	The supplier will be responsible to supply and thereafter installation of the Power Module for APC UPS.

(NADEEM ANWAR)

Manager (P&I)

2nd floor, Software Technology Park (STP), I-9/3, Islamabad.

Ph: 051-9259354, 051-9259353

Email: nadeem.anwar@pral.com.pk

ANNEXURE-A

SCHEDULE OF REQUIREMENT

TENDER # P-30 DATED 13-12-2018

Power Module for APC UPS

Scope of Work

After careful evaluation of the market, PRAL invites APC Authorized partner only to respond to our Request for Proposal (RFP) for the Supply of APC Symmetra Modular UPS Power Modules. This RFP document sets out the requirements and the selection criteria to be used in the evaluation and provides information regarding how the process will be managed.

Supplied Power Modules should be brand new and genuine in all respects. Replacement warranty to be provided.

Technical Requirement

# APC Symmetra PX Power Module, 10/16kW, 400V

## SYPM10K16H

APC Symmetra PX Power Module, 10/16kW, 400V

A 16kW high efficiency power module for the Symmetra PX160kW & PX48kW. This power module is backward compatible with the SYPM10KH module and will autodetect to deliver only 10kW of power protection if installed in a PX80kW, 40KW or 20kW all-in-one.

#### SYPM10K16H Features

APC Symmetra PX Power Module, 10/16kW, 400V

- Input power factor correction

Minimizes installation costs by enabling the use of smaller generators and cabling.

- Modular design

Increases adaptability with an open architecture configurable to any IT environment.

TECHNICAL SPECIFICATIONS

#### Output

- Output power capacity 16.0 KWatts / 16.0 kVA

- Max Configurable Power (Watts) 16.0 KWatts / 16.0 kVA

- Nominal Output Voltage 230V , 400V 3PH

- Output Voltage Note Configurable for 380 : 400 or 415 V 3 Phase nominal output voltage

- Efficiency at Full Load 95.0 %

- Output Voltage Distortion Less than 2%

- Output Frequency (sync to mains) 50/60 Hz +/- 3 Hz user adjustable +/- 0.1

- Output Frequency (not synced) 50Hz +/- 0.1% for 50Hz nominal

- Load Crest Factor Unlimited

- Topology Double Conversion Online

- Overload Operation 10 minutes @ 125% and 60 seconds @ 150%

- Output Voltage THD < 2% for 0 to 100% linear load and < 6% for full nonlinear load

#### Output Voltage Tolerance +/-1% static and +/- 5% at 100% load step Input

- Nominal Input Voltage 400V 3PH

- Input frequency 40 - 70 Hz

- Input Connections Hard Wire 5-wire (3PH + N + G)

- Input voltage range for main operations 340 - 477V

- Efficiency at Full Load 95.0 %

- Input Total Harmonic Distortion Less than 5% for full load

- Maximum Short Circuit Withstand (Icw) 30.0kAmps

- Maximum Input Current 33.0A

- Input Power Factor at Full Load 0.99

#### Physical

- Maximum Height 132mm , 13.2CM

- Maximum Width 483mm , 48.3CM

- Maximum Depth 700mm , 70.0CM

- Rack Height 3U

- Net Weight 28.5KG

- Shipping weight 31.55KG

- Shipping Height 225mm , 22.5CM

- Shipping Width 595mm , 59.5CM

- Shipping Depth 700mm , 70.0CM

#### Environmental

- Operating Temperature 0 - 40 °C

- Operating Relative Humidity 0 - 95 %

- Operating Elevation 0-999.9meters

- Storage Temperature -15 - 40 °C

- Storage Relative Humidity 0 - 95 %

- Storage Elevation 0-4500meters

- Audible noise at 1 meter from surface of unit 63.0dBA

- Online thermal dissipation 2573.0BTU/hr

- Protection Class NEMA 1

#### Conformance

- Approvals CE, EN 50091-1, EN 50091-3, FCC Part 15 Class A, VFI-SS-111

Bill of Quantity

| Sr. # | Description | Quantity |
| --- | --- | --- |
| 1 | Power Module for APC UPS | 3 |

ELIGIBILITY CRITERIA

| Sr. # | Criteria | Compliance | Documents to be provided by the bidder |
| --- | --- | --- | --- |
|  | Bidders who have been black listed/ debarred by any govt. Dept. shall not be considered. An affidavit to this effect shall be submitted by the consultant/consulting bidder duly attested by authorized signatory. |  | Undertaking certificate from THE BIDDER |
|  | The Bidder shall furnish as part of his bid, a Call Deposit/Pay Order equivalent to 2% of the overall cost Earnest Money crossed in favor of “Pakistan Revenue Automation Limited”. Any bid not accompanied by 2% Earnest Money shall be rejected without any right of appeal. |  | Call Deposit/Pay Order equivalent to 2% of the overall cost. |
|  | Partnership with OEM |  | Valid partnership proof with OEM |

General Terms and Conditions

- The warranty and onsite support of the proposed hardware is required for a period of three years

- The prices should be valid for 180 days.

- PRAL reserves the right to accept any bid or reject any or all bids without assigning any reasons whatsoever.

- For All Zero Rated or Exempt Items/Supplies, relevant S.R.O/Circular must be attached with the Quotation.

- This RFP does not commit us to award a contract, to pay any costs incurred in the preparation of a response to this request, or to procure or contract for services or equipment.

- No advance payments are payable, payments will be made on after verification and issuance of Job Completion Certificate.

- Service Provider shall provide service and response engineers mobile numbers to PRAL for direct support during office and off hours.

- Government duties and taxes should be separately mentioned in the Financial Proposal, if applicable.

- The decision for the award of Contract cannot be challenged anywhere

- The firms black-listed/ debarred in participating in any procurement activities in Pakistan are not allowed to bid.

- Earnest money of the unsuccessful bidders will be returned after award of contract.

- Bidder who has been awarded contract / work orders can get the earnest money released after successful commissioning and issuance of Job Completion Certificate.

- All supporting documents MUST be provided, where applicable.

- Product brochures should also be attached.

- Vendor must provide evidence of partnership letter with OEM.

ANNEXURE-B

BIDDING FORM

##### Date: _________								           Tender No. P-30/2018

Pakistan Revenue Automation (Pvt.) Limited, Islamabad.

Gentlemen,

1.	Having examined the conditions to Tender and Specifications of Tender P-30/2018 dated            13-12-2018 the receipt of which is hereby acknowledged we, the undersigned, offer to install, supply and deliver in conformity with terms and conditions and specifications mentioned in Tender for the sum of Rs._________________________ (Rupees _____________________________) or such other sums as may be ascertained in accordance with the said Conditions.

2.	If our Bid is accepted we shall deliver the equipment specified in the Tender Documents within ___________ from the date of receipt of your contract.

3.	We agree to abide by the terms and conditions of the Tender for the period of _______ from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.

4.	Until a formal Purchase order(s) is placed, this Bid, together with your written acceptance thereof, shall constitute a binding contract between us.

5.	We understand that you are not bound to accept the lowest or any proposal you may receive or to inform us of the rejection of our bid or to give any reasons therefore.

Dated this ______________ day of _______________________ 2018_______________

Signature_______________________ in the capacity of __________________________ duly authorized to sign Tender for and on behalf of

___________________________________________________________________________________

(NAME OF FIRM IN BLOCK CAPITALS)

Complete address: ___________________________________________________________________

Fax No._________________________ Telephone No.___________________________

(SIGNATURES)

Witness: -

- _______________________

- _______________________